## Slide 1: RTLS Support Update
Outage evidence and the path to Tier I support
August 2026

## Slide 2: Support operations
Recurring outage pattern
and transition to the InfoLink service model

## Slide 3: IDF power events drive recent anchor outages
DATE | SITE | TRIGGER | OPERATIONAL IMPACT | RECOVERY
Jun 4 | CVG2 | Site maintenance / power loss | Bridge + anchors offline | Restart CUWB
Jun 7 | STL3 | IDF UPS down | 28 anchors disconnected | Bypass IDF UPS
Jun 14 | CMH3 | IDF outage | Vehicles unavailable in some areas | Restart CUWB
Jul 12 | CMH3 | IDF outage | Areas unavailable | Restart CUWB
Aug 4 | YY79 | Holiday power cutoff | Slow vehicle movement | Restart CUWB
Aug 10 | CMH2 | Likely IDF restart | Slow vehicle movement | Self-recovered
RECURRING PATTERN
IDF power event
Anchors offline / out of sync
Vehicle performance degrades
OPERATIONAL IMPLICATION
Tier I can resolve the common path with a standard runbook
STANDARD RESPONSE
Confirm power -> resync anchors
Escalate unresolved cases
ACTION: Adopt the standard response to restore service faster and reduce repeat cases.
Source: support cases, Jun-Aug 2026

## Slide 4: Tier I moves to InfoLink in Q1 2027; Tier II remains interim coverage
CURRENT STATE
BUILD NOW
TARGET STATE
Tier II support
Monday-Friday, 8 AM-5 PM EST
After-hours anchor issues
Use bypass mode
Amazon local resource
Powers down the bridge
No cost
Until Tier I services are established
Crown RTLS support tools
Automatic notification
For anchor and truck issues
Controlled system restart
Standard recovery workflow
Target readiness
Q1 2027
Tier I through InfoLink
Call Center ownership
Covers every reported issue
Common Tier I path
First-line recovery
Before Tier II escalation
INTERIM OWNER ACTION
Confirm the local bridge shutdown contact
TIER I QUOTE INPUTS
Response time | Coverage window
Number of sites in scope